Low Carbon Concept Appraisal, Soneva Fushi, Six Senses

by The Carbon Advisory Service Ltd.

December 2009

Revision history

| Issue No. | Status | Date | Author | Reason for issue |
| --- | --- | --- | --- | --- |
| 1 | Work-in-progress | 15th Sept. 2009 | Darren Ball | Client comment |
| 2 | Draft | 30th Oct. 2009 | Darren Ball | Prior to presentation |
| 3 | Final | 17th Dec. 2009 | Darren Ball | Client issue |
| 4 |  |  |  |  |
| 5 |  |  |  |  |

Contents

1	Summary	1

2	Introduction	3

3	Causes of On-site Carbon Dioxide Emissions	4

4	Zero-carbon energy strategy	8

4.1	General	8

4.2	Tri-generation	9

4.3	Biofuels	11

4.3.1	Biodiesel	11

4.3.2	Biogas	13

4.3.3	Conclusion	14

4.4	Photovoltaics	14

4.5	Solar-thermal domestic hot water (DHW)	16

4.6	Anaerobic digestion	17

4.7	Electricity to laundries	19

4.8	Kitchens	21

4.9	Lighting	22

4.10	Wind power	23

4.11	Desalinated water	24

4.12	Biochar	28

5	Analysis and Results	30

5.1	Method and approach	30

5.2	Current scenario plus additional cooling to host accommodation	30

5.3	Cooling to host accommodation added	32

5.4	Demand reduction, solar-thermal, DHW, PV and anaerobic digesters	33

5.5	As 5.4 but tri-generation added	34

5.6	Energy monitoring and reduction	35

5.7	Biodiesel	35

5.8	Biochar	35

5.9	Methane sequestration	Error! Bookmark not defined.

6	Recommendations	37

7	Appendix A – Calculation of proposed CO₂ emissions factors	41

8	Appendix B – energy modelling	43

8.1	Thermal modelling	43

8.2	Lighting calculations	56

9	Appendix C – weather data	58

# Summary

This report describes how Soneva Fushi’s on-island energy usage can be reduced to zero carbon emissions.  The strategy relies upon the following principal features:

- Reduce energy consumption through simple energy-efficient measures, such as better light-switching, efficient use of potable water, better energy metering and thorough energy auditing.

- Provision of site-wide solar-thermal domestic hot water (DHW).

- Procurement of “ethical” biodiesel.

- Switching from electricity to solar-thermal DHW or biogas wherever possible in kitchens, laundries and other DHW usage.

- Installation of 70 kW photovoltaics panels (already installed).

- Replace the existing electrical generators, which are too large, with smaller biodiesel-fired Combined Heat and Power (CHP) units.

- Provide an island-wide chilled water network with central absorption chillers powered from the waste heat off the new biodiesel CHP units and water-cooled using a refurbished seawater system.

- Biochar all branches and other “woody” biomass.

- Use organic digesters to gasify food waste and “leafy” biomass.  The gas is then used to displace LPG and/or to reduce electrical loads through micro CHP – all dependent upon further analysis of the loads profiles.

- Progressively introduce PV modules on the flat roofs of host areas, especially as battery technology improves and prices reduce.  This will have the effect of reducing the output of the tri-generation plant.

- New villas to be built to higher standards of air permeability to reduce cooling loads on the tri-generation plant, especially as output reduces with the higher deployment of PV.

- If necessary, provide an alternative heat source for the absorption chillers as the heat from the CHP plant progressively reduces with the further deployment of PV over time.  This could be concentrated solar power, evacuated tubes or hydrogen fuel cells.

The writers are aware that much controversy exists around the use of biofuels (liquids, solids and gases) in terms of their effects on ecosystems, world food prices and deforestation.  CAS has gone to considerable lengths to ensure that none of these criticisms can reasonably be applied to the recommended biofuel, in this case, a biodiesel.

Opportunities for manufacturing ethical biofuels are finite and there is sufficient biofuel to support only a small portion the world’s energy needs.  Therefore biofuels, even ethical ones, should not be used as a lazy alternative to fully optimised low-energy design.

Approximately half the estimated reduction in CO₂ emissions was achieved through energy efficiency measures, systems integration, renewables and greenhouse gas (GHG) sequestration.  Most of the remaining load is as yet unidentified electrical usage to which the biodiesel-powered electrical generators have been applied.

A significant recommendation of this Concept Appraisal is to undertake a detailed electrical survey of the island to fully understand where electricity is being used – only then will it be possible to devise further efficiency measures and reduce the dependency on biofuel.

The proposed energy strategy is a lose fit of a number of interrelated individual elements, and is designed to enable different features to grow or shrink over time, allowing the system to evolve and morph as technologies mature and local/global circumstances change.

# Introduction

Six Senses has announced a plan to make their Soneva Fushi resort zero-carbon.  This Concept Appraisal report focuses on the on-island emissions and seeks to identify the optimum blend of technologies required to achieve this target.

Soneva Fushi is a luxury five star holiday resort in the Maldives with an uncompromising focus on quality, quest experience and relaxation of body and mind.  It is in this context that this energy strategy has been prepared.

CAS’s initial instruction was two-fold:

- Provide an outline design for a centralised chilled water system making use of the seawater pipework and existing fan-coil units.

- Provide an outline design for an improved domestic hot water network.

After the completion of these two outline designs, CAS would be appointed as Concept Guardians to ensure that the design development and installation work was faithful to the concept.

However CAS recommended that prior to the commencement of the above process, a Concept Appraisal document was produced to explore relevant technologies necessary to deliver a zero-carbon energy strategy for Soneva Fushi’s on-island activities.

There are scores of different low-carbon technologies, and exponentially more hybrids and combinations.  Any report attempting to demonstrate the advantages and disadvantages of them all would have an encyclopaedic quality, rather than being focused on the actual project.  For this reason, CAS has used its experience and professional judgment to concentrate effort on suitable options.

During discussions with Six Senses staff and other consultants, questions have been raised about some of those options CAS chose not to include. Those questions are answered in this revision.

All else being equal, mature technologies that are well understood will be preferred over those which are young and emerging.  The largest energy reduction measures identified here use decade-old technology, and in some cases, over a century old.

With thoughtful integration of simple ideas, emissions can be avoided without recourse to expensive high-tech products.

This report has been prepared fully cognisant of the fact that any recommendations adopted will have to be implemented as retro-fits.  If this was a brand new resort, or if existing buildings were being replaced, then alternative options would become cost-effective.  For instance, alternative construction standards might be used when villas are replaced.  But to modify the existing stock in meaningful ways is unlikely to be viable.

# Causes of On-site Carbon Dioxide Emissions

Six Senses commissioned a carbon audit of Soneva Fushi from energy consultants Carbon Foresight.  Carbon Foresight submitted their report on 24th February 2009.  Using information from the report, CAS has produced the pie chart presented below.

Chart 3.1 – Annual emissions, tonnes CO₂ equivalent

CAS’s Concept Appraisal is targeting emissions from energy used on the island, which from the chart would be the electrical power (2,950 tonnes CO₂ equivalent) and the RO plant (274 tonnes CO₂ equivalent) equating to a total of 3,224 tonnes CO₂ equivalent out of a overall total of 24,754 tonnes CO₂ equivalent (13 percent).

Even more recent than this study were calculations undertaken by Ms. Anke Hofmeister of Six Senses for the year ending July 2009.  Because these calculations cover a different period, the results are slightly different.

Ms. Hofmeister’s figures, hereafter the Six Senses Carbon Calculator Audit (SSCCA) figures, are preferred to Carbon Foresight’s because they are both more current and more detailed.

The relevant energy usage figures from the SASCCA, together with the associated CO₂ emissions, are reproduced in table 3.1 below.

| Fuel | Quantity |  | Carbon emission factor |  | Total emissions |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Diesel | 1,375,564 | litres | 2.639 | kg CO₂ / litre | 3,630 | tonnes CO₂ |  |
| LPG | 51,794 | kg | 2.932 | kg CO₂ / kg | 152 | tonnes CO₂ |  |
|  |  |  |  | TOTAL | 3,782 | tonnes CO₂ |  |
| Table 3.1 – CO₂ emissions from on-site energy use, July 2008 to June 2009 (source: Six Senses, SSCCA) |  |  |  |  |  |  |  |
| Note; 1 tonne = 1000 kg |  |  |  |  |  |  |  |

| Fuel | Carbon emissions factor |  |  |
| --- | --- | --- | --- |
| Diesel | 0.263 | kg CO₂/kWh |  |
|  | 2.639 | kg CO₂/litre |  |
|  | 3164 | kg CO₂/tonne |  |
| LPG | 0.225 | kg CO₂/kWh |  |
|  | 1.495 | kg CO₂/litre |  |
|  | 2.932 | kg CO₂/kg |  |
| Petrol | 0.252 | kg CO₂/kWh |  |
|  | 2.304 | kg CO₂/litre |  |
|  | 3423 | kg CO₂/tonne |  |
| Electricity | 0.834 | kg CO₂/kWh |  |
| Water | 4.688 | kg CO₂ per m³ |  |
| Table 3.2 - Project CO₂ emissions factors |  |  |  |  |
| (source: Appendix A) |  |  |  |

No data are included in table 3.1 for electricity because electricity is generated on site using diesel-powered generators.  However the comparable figure for electricity is 4,355,346 kWh

In summary, emissions from on-site energy usage for the year ending June 2009 was 3,782 tonnes CO₂.

Also useful to note is that purified water, using reverse osmosis (RO), requires 5.62 kWh electricity per cubic metre.  This was calculated by dividing the metered electricity use by the water produced over the same 12-month period.

In order to reduce energy consumption, and therefore carbon emissions, it is useful to know as much as possible about where energy is being used.  Several different methods were used to add some breakdown to the total energy usage figures provided by the SSCCA.

| Usage | Quantity | Fuel | CO₂ Factor | Total emissions | Source |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | (MWh) |  | (t.CO₂/MWh) | (tonnes CO₂) |  |  |  |
| Cooling | 1,096 | Electricity | 0.834 | 913 | Modelling, Appendix B |  |  |
| Kitchens | 600 | Electricity | 0.834 | 500 | Metered |  |  |
| Kitchens | 675 | LPG | 0.225 | 152 | Calculated from Ms. Hofmeister's data) |  |  |
| Laundry | 225 | Electricity | 0.834 | 188 | Metered |  |  |
| Water (RO) | 373 | Electricity | 0.834 | 311 | Metered |  |  |
| Lights | 468 | Electricity | 0.834 | 390 | calculations, Appendix B |  |  |
| Other | 1,594 | Electricity | 0.834 | 1328 | Deducted from total |  |  |
| TOTAL | 5,030 | NA | NA | 3,782 | Metered |  |  |
| Table 3.3 – Energy and CO₂ breakdown |  |  |  |  |  |  |  |

Graph 3.2 – breakdown of annual CO₂ emissions (tonnes).  As table 3.3

Note that there is a significant amount of electricity unidentified.  Without knowing what it’s used for, no mitigation measures can be proposed.  Adding further resolution to this number is a major conclusion of this report.

Further resolution is added to the figures by understanding when energy is used and the coincident population of the island.  The SSCCA’s electricity data was provided monthly, therefore using a combination of sub-metered data, calculations and computer-based energy modelling, CAS were able to produce graphs 3.3 and 3.4.  For details of the energy modelling and calculations, reference should be made to Appendix B.

Graph 3.3 – mothly electricty usage (kWh)

Graph 3.3 is showing the significance of the unidentified electricity usage (the grey bar at the base).  The ploted line shows the total population of the island (hosts and guests) which correlates very well with the energy consumption: a good sign that energy is being well managed.

Graph 3.4 – Monthly electricity usage (kWh/night)

Graph 3.4 is showing the monthly electricity consumption per night-stay (hosts and guests).  All other things being equal, one would expect the electricity consumption per night-stay to be lowest when the population is highest and vice versa, and with the exception of May and June, that is what graph 3.4 is showing.

Ignoring May and June, the total electricity consumption (shown by the top of the stacked bars), and the population profile (shown by the plotted line)are following damped sinewave-type profiles but inverted relative to each other (population up, energy per night down).

The results for May and June buck this trend by having low electricity consumption and low occupancy simultaneously, suggesting that improvements have been made to the site since May 2009.

Individual profiles for kitchens, laundry, water and LPG also broadly follow these trends.  Graphs for these are shown in Section 4 – Zero-carbon energy strategy, under the relevant sub-headings.

# Zero-carbon energy strategy

## General

It is sometimes popular to explain low- and zero-carbon energy strategies by differentiating between supply and demand measures and then neatly attributing to each measure its own proportional contribution.  Whilst this approach is convenient and simple, it is usually inaccurate and misleading.

Energy strategies are not like balance sheets with lists of disparate line-items that can be added or omitted at will; rather they are inter-dependant ensembles in which each individual part has an impact on the whole and vice versa.

The benefit of individual components cannot be stated other than in the context of the whole integrated system.  For instance the PV appears to reduce the load on the electrical generators by 153 MWh per year, this being equal to their anticipated electrical yield.  However, once the complex inter-dependencies of the entire energy strategy are considered, the actual estimated saving is reduced to 122 MWh (20 percent less).

It can also be misleading to try and differentiate between demand savings and better supply strategies, because again these are intertwined.  For instance, the benefit of introducing solar-thermal domestic hot water (a supply strategy) will be affected by whether or not electric water heating is used in the kitchens (a demand strategy).

The entire energy strategy, including supply and demand measures, is described in this one section.  When attributing benefits of individual measures, the figure quoted is the difference between the entire strategy with and without the particular measure incorporated.

## Tri-generation

The most common way to generate electricity in the Maldives is with electrical alternators driven by diesel-fired internal combustion engines.  Anybody who drives a car will know that internal combustion engines get very hot and this heat has to be rejected.

The engine is cooled by water circulating between the engine and a heat exchanger, erroneously called a “radiator”.  A fan draws cooler ambient air over the radiator thereby rejecting the engine’s surplus heat to atmosphere.  This is necessary to protect the engine from overheating, but even after all of this, the engine is still very hot.

At Soneva Fushi, the radiator circuit is used to heat Domestic Hot Water (DHW), which is a good way of reclaiming some of this lost heat, but it is possible to do much more.

If in addition a water jacket was put around the engine and alternator, even more heat could be collected at around 95 °C and put to good use around the island.  Generators that reclaim heat in this way have been around for many decades and have traditionally been called “Combined Heat and Power” (CHP) units.  Again this term is somewhat erroneous because heat and electricity are both power, and so they have more recently been called “co-generation” units.

Paradoxically, heat can be used to generate cooling.  The most common way of doing this is through an absorption chiller.  When heat off an electrical generator is used to drive cooling it is called tri-generation.

The thermodynamic cycle of an absorption chiller is very similar to that of a domestic refrigerator but where heat, rather than an electrically-powered compressor, provides the motive power.  In fact absorption cycle refrigerators are commonly used in camping and caravanning.

One disadvantage with absorption chillers is that they are less efficient, but this is no matter if the heat source is free.

All chillers have to reject the heat they absorb to a heat sink of some kind – usually ambient air.  The higher the temperature of the heat sink, the more energy the chiller will need to consume to keep itself cool – again this is true of all chillers.  But in the case of an absorption chiller, where the motive power is heat, there is an additional factor to consider: not only does the chiller require more heat in hot environments, but it also requires heat at a higher temperature.

With the available heat source of the generator sets (around 90 °C), an air-cooled absorption chiller would require an ambient dry-bulb temperature of no more than about 28 °C.  Unfortunately the maximum dry-bulb temperature of the Maldives is around 35 °C.

If water-cooled, the maximum cooling water temperature would be around 33 °C.  To achieve 33 °C with cooling towers or evaporative coolers (despite many other objections), the ambient wet-bulb temperature would need to be around 28 °C.  Unfortunately the maximum wet-bulb temperature in the Maldives is about 30 °C.  However to water-cool the chillers using seawater, the seawater would need to be no warmer than about 31 °C.  Fortunately the actual temperature peaks at around 19 °C (depending upon depth).

According to the energy modelling (see Appendix B), cooling represents about one-quarter of the island’s total electricity demand, of which about 85 percent can reduced by the adoption of the tri-generation system.

Further, at times when the cooling load is low, the generators will be able to divert their waste heat to replenish domestic hot water calorifiers, thereby reducing energy consumption further.

By far the tri-generation option is the most significant of the carbon reduction measures identified, but its deployment is dependent upon the partial reinstatement of the deep seawater pipe (the depth to be determined).

Notwithstanding the benefit of the tri-generation plant, Soneva Fushi is not going to get to Carbon-zero by burning diesel, therefore the fuel source need to be reconsidered (refer to sub-section 4.3, biofuels)

Figure 4.2.1 – Tri-generation schematic

Currently Soneva Fushi has four diesel-powered electrical generators; three at 360 kW and one at 800 kW.  The base load of the island is currently about 500 kW which means that whenever the load goes slightly above the base, two 360 kW generators or one 800 kW generator are required to operate at approximately half their capacity.  This is a very inefficient way to run the generators and is a result of the generators being over-sized.

It would have been better if the generators had been sized much smaller to allow a closer match between supply and demand.  If the energy reduction strategies suggested in this report are implemented, the problem of over-sizing will be exacerbate further with the likely scenario of one generator operating almost continuously at low load.

A full peak load analysis is outside the scope of a Concept Appraisal, but it is likely that the peak load will be around 600 kW and the base load about 300.  Based on these figures (which are only approximate at this stage), the recommendation would be to use four CHP units, each rated at 175 kW.

At base load two generators would operate at about 85 percent load.  If the load slightly exceeds the output of two generators, then the third generator will be called and all three will operate above two-thirds load.  When the load exceeds the output of three generators a fourth generator will be called an all four will operate above three-quarters load.

One of the existing 360 kW generators should be retained as a standby unit in case of failure or maintenance.

Currently the generators are sequenced manually but for the tri-generation plant to work they would have to be sequenced automatically.

The long term strategy, as shall be discussed in subsequent sections, is to progressively generate less electricity from traditional generators/CHP and more from battery-backed photovoltaics.  As this happens, alternative heat sources must be identified to power the absorption chillers.  Options are concentrated solar, evacuated tubes or waste heat off hydrogen fuel cells.

By maintaining the centralised absorption cooling option, the size of the PV and battery array is significantly reduced.

## Biofuels

To achieve the desired ‘zero-carbon’ status, it will be necessary for Soneva Fushi to end its reliance on diesel fuel for electricity generation.   The new ‘green-powered’ CHP plant (combined heat and power) will generate not only electricity, but also valuable waste heat which will operate the cooling systems on the island.  This generator plant can be fuelled using a readily available and sustainable biofuel: biodiesel.

### Biodiesel

Biodiesel is a renewable fuel similar to petroleum-based or ‘fossil’ diesel.  CO₂ is released when burnt, but this is only the CO₂ that was recently absorbed, making the cycle carbon-neutral overall.

Energy is used in the harvesting, processing and transportation of the biofuels, and if conventional hydrocarbon fuels are used for these activities, which is commonly the case - at least with transportation - then overall the fuels retain some carbon footprint.  In principle it should be possible to avoid all of these carbon emissions by using some of the biofuel to power each of these activities, but for the purposes of this study, a CO₂ emissions factor of 0.025 kg CO₂/kWh (the figure used in the UK Building Regulations) has been allowed.  This figure should be calculated more precisely when selecting suppliers.

Biodiesel can be produced from vegetable oil, animal oil/fats, tallow and waste cooking oil.  Biodiesel contains almost as much energy as its fossil counterpart but does not produce the black ‘smoke’ associated with burning fossil diesel.

One notable advantage to biodiesel is that it can be used in conventional diesel engines, such as for automobiles and boats.  The use of biodiesel in a conventional diesel engine results in a substantial reduction of unburned hydrocarbons, carbon monoxide, and particulate matter compared to emissions from diesel fuel.  In addition, the exhaust emissions of sulphur oxides and sulphates (major components of acid rain) from biodiesel are essentially eliminated compared to diesel.

Acquisition of Biodiesel

The subject of biofuels has aroused controversy in recent years, due to ‘food crops’ being harvested for fuel, or ‘fuel crops’ using arable land which could be used to solve the food crisis.  Some countries have started using corn, soya, rape, grains and sugar cane for production of biofuels, thus causing diversion of food resources into fuel.  This has created serious pressures on global food markets.  CAS is very aware of this problem, and has conducted extensive research into the production and export of biofuels from India.

There are companies in India and elsewhere producing and exporting biofuels using socially responsible, sustainable methods.

One such crop is Jatropha Curcas - a non-edible oilseed tree suited to cultivation on dry, marginal lands which are unfit to sustain food crops.  Jatropha is a hardy, long-lived perennial which can help restore degraded landscapes.  More importantly, Jatropha's oil does not compete in the food-fuel debate as the non-edible oil can only be used towards biofuel production.

CAS is able to access a number of ethical Jatropha fuel suppliers, through a relationship with Imperial College London, and will do so when required on commencement of the next stage of the project.

Switching to biodiesel from a socially responsible and sustainable supplier will not only lower Soneva Fushi’s carbon footprint, but help Indian farmers and communities out of poverty.

Jatropha is only one example, but there are alternatives, such as recycled cooking oil.

Scalability

All renewable energy sources are a finite, usually because there is a limit to the number of suitable sites.  This is why all realistic suggestions to transition to a zero carbon economy involve using a wide combination of methods.  The mantra is: do whatever you can, where you can.

Ethically sourced biofuel cannot be produced in sufficient quantities to power the whole world, and so it is necessary to wisely use what can be produced.  Ultimately, it might be that the wisest place to use biofuel is in aviation where there are very few choices, but that is not yet the case.

The aviation industry is exploring biofuels and there has been a successful flight using coconut and babassu oil-derived biofuel in an unmodified Boeing 747.  The flight caused a storm of criticism from environmental campaigners, and it’s obvious that huge environmental damage would be caused if the aviation sector sought to power their fleets exclusively from nuts.  But this was not the intention.  The purpose was to prove the technology, but the ultimate intention is to use algae.

If Six Senses use ethical biofuel, such as Jatropha; in addition to generating low- or zero-carbon electricity, hot water and cooling; they will also provide an income stream to small farmers.  If in years to come it is found that the fuel is better used for aviation, then Six Senses will at least have been instrumental in stimulating the supply chain.  There is no sense in not using ethically sourced biofuel in the interim period because the aviation industry might one day need to make use of it, only to find that when they do, they don’t use Jatropha at all but algae.

As shall be seen in subsequent sections, the technologies proposed for Soneva Fushi are completely integrated and varied.  For a number of reasons, not least amongst them is fuel cost, there is merit in progressively reducing dependency on biofuels as other technologies (such as PV and hydrogen fuel cells) mature further and reduce in price.

The strategy is to evolve the island-wide system over time to progressively wean Soneva Fushi off biofuel before the ethical biofuel production is maximised.

Storage of Biodiesel

The standard storage and handling procedures used for petroleum-based diesel fuel apply to biodiesel.  Compared to petroleum-based diesel, biodiesel fuel has lower oxidation stability, and there are greater concerns for water contamination within the storage tank and microbial growth.  Biodiesel should be stored in a clean, dry, dark environment.  Acceptable storage tank materials include aluminium, steel, fluorinated polyethylene, fluorinated polypropylene or Teflon®.  Storage containers which contain copper, brass, lead, tin or zinc should not be used.  Every effort should be taken to make sure that the Biodiesel product is used within six months of the date of manufacture.

Cost of biodiesel

The cost of biodiesel varies with market rates and is expected to fall with increased demand and production.  The typical price of a litre of biodiesel is about US $0.50.  For Soneva Fushi’s current demand, the annual spend would be circa US$690,000.  The energy savings identified in this Concept Appraisal would reduce this spend by about half.

### Biogas

Another way in which the CHP plant could be fuelled is by importing bamboo (or other organic material) to make biogas.

Biogas is a combustible gas created by anaerobic decomposition of organic material, or through pyrolysis (burning in the absence of oxygen).  Biogas is composed primarily of methane and carbon dioxide, with trace other gases.

Acquisition of Biogas

Unlike biodiesel, biogas cannot be imported and must be generated and consumed at the place of production.

To achieve this, Soneva Fushi would require a pyrolysis plant to manufacture the biogas, and a constant supply of organic material to fuel it.  Bamboo, or any other biofuel, would have to be transported to the island in its bulk form.

Storage of Biogas

Unlike LPG (liquefied petroleum gas), which liquefies at 11.5 bar, biogas requires a pressure of 36 bar for liquefication.   Propane storage tanks can only be used up to about 14 bar; higher pressures are complex, expensive and dangerous.  This is why the import and export of biogas is unfeasible.

Biogas can be stored for short periods (a couple of days at most) in rubber balloon-like devices, but it is extremely voluminous and highly combustible.  It is colourless, lighter than air, and difficult to detect.   A full-time gas engineer would be required to monitor the safe storage of any biogas, and monitoring and alarm systems would need to be extensive.  Storing any more than small amounts would be comparable to having a Hindenburg on the island.

For this reason, storage is not recommended, and a constant creation/consumption process would be required.  Employees would be required to ‘feed’ the pyrolosis plant round-the-clock to assure non-interrupted electrical supply.   Approximately seven tonnes of bamboo would be required per day to meet the island’s electricity demands with biogas.

Cost of biogas:

Pyrolysis generator plant:  US$900,000

The cost of raw bamboo varies widely but an average assumed market rate of $40/tonne would work out to approximately $200,000 per year, plus shipping costs, for the current energy demand or about half this after energy reduction measures have been implemented.

### Conclusion

Considering added cost of the pyrolysis plant, the import, storage, and handling of bamboo, the additional staff requirements, the danger of biogas storage, and the fact that responsible and sustainable biodiesel is readily available, biogas-powered electrical generation is not recommended for Soneva Fushi.

A third way in which the CHP plant could be fuelled is by importing bamboo (or other organic material) to burn as biomass, fuelling a steam-powered turbine.  This would require a large steam-generating plant with high maintenance to generate enough electricity to power the island.  A suitably qualified steam engineer would have to be in regular attendance to certify the plant’s safety and there would be similar issues of staffing and fuel handling.  Again, this would be an inappropriate technology for a small holiday island and is not recommended.

## Photovoltaics

A photovoltaics array was supplied and installed by Earth Link Ltd in parallel with the production of this Concept Appraisal.

Technical information about the PV modules were supplied by Earth Link (Dr. Lounette Dyer) and reproduced below:

- Seasonal average efficiency, 10.4%

- Electronic losses (inverters, sync panels, etc), 15%

- Module area, 750 m²

- Inclination for horizontal, 6 degrees

Using hourly-annual global radiation figures from a weather file of the neighbouring island of Minicoy, CAS calculated the annual electricity yield to be 153 MWh.

Earth Link had previously advised that the yield would be 151 MWh per year, which is virtually identical to the CAS analysis.  The CAS analysis produced outputs for each hour of the year, which is useful when integrating systems as well as providing an independent verification of Earth Link’s proposals.

Using the factor of 0.834 kg CO₂/kWh for electricity generated on site, 153 MWh of carbon-free electricity avoids 128 tonnes CO₂ (3.4 percent of total).  However, because of the way in which systems integrate with each other, the actual benefit is a little smaller than this.

By far the most significant energy-efficiency saving is the use of waste heat to off the electrical generators to provide motive power for the site-wide chilled water system.  PV reduces the demand for electricity generation, but in doing so it also reduces the available waste heat, and therefore the availability of ‘free’ chilled water.  It is better to have the PV than not to, but the after considering this effect the benefit drops to 102 tonnes CO₂ (2.7 percent of total).

In order to meet the entire island’s electricity demand from PV would require battery back-up.  Neglecting the charging efficiency of the batteries, the size of the photocell array would be 21,375 m² with a peak output of 2,000 kW and a cost of circa $8m (excluding battery cost).

Using Earth Link’s figures, 1 m² of PV generates circa 200 kWh per annum, costs circa $373 (excluding batteries), and lasts for 25 years.  Using simple payback only, the cost per kWh is $0.0746.

Making allowance for financing costs would obviously significantly increase the unit rate, but on the basis of these numbers, this is a very cost-effective technology - especially in the Maldives where the alternative is diesel-powered generators.

Pivotal to this analysis however is that the unit price of $373 per m² includes, not just for the PV panels, but also for site preparation, delivery, construction, installation, framing, groundworks, synch panels and inverters.

The short-term strategy is to monitor the performance of the small-scale installation with a view towards extending the system over time, especially as battery technology improves and prices reduce.

Rather than one large centralised battery installation, batteries could be distributed around the island within individual buildings.

Irrespective of the apparently good unit rate, the capital cost and space take are very high and therefore measures that reduce energy demand should be pursued.

## Solar-thermal domestic hot water (DHW)

Currently, most of the heat for the domestic hot water (DHW) is supplied from the diesel generators’ radiators, which is quite a crude version of Combined Heat and Power (CHP).  In the proposed energy strategy, all of this heat will be required to power absorption chillers to serve the site-wide district cooling system – therefore an alternative heat source is required.

Hot water within the restaurants is supplied by electric emersion heaters.  According to the data received from the SSCCA, there are about 300,000 meals per year.  According to the CIBSE Guide G and the British Institute of Plumbing guide, on average each meal would require six litres of hot water at 60 °C.  The energy required to raise six litres from mean ambient air temperature of around 28 °C to 60 °C is:

6 kg x 4.2 kJ/kg.K x 32 K = 806 kJ

300,000 meals x 806 kJ/meal = 242 GJ (Gigajoules) or 67 MWh.

To put this in context, these couple of water heaters are using more than half the electricity generated by the new photovoltaic array.

An unknown amount of electricity is being used to generate hot water within the laundries, but the connected electrical load within the laundries for hot water and clothes washing alone is 141 kW – that’s double the peak output of the photovoltaic system

It’s as if all 750 m² of photovoltaic modules are being used to convert solar energy into electricity at 10 percent efficiency and then back into heat.

Again there are no data on the island’s annual DHW loads, but according to the British Institute of Plumbing, a five star hotel has a daily DHW demand of 135 litres per bedroom.  Applying this figure to 192,816 night-stays gives an annual demand for DHW of 26,030 m³ (about 40 percent of total water usage).

Approximately 1,000 m² (say 32m x 32m) of simple flat-plate solar collector would be sufficient to provide the complete DHW needs of the entire island.

Solar collectors could be located upon the roof of a new plantroom building used to accommodate the absorption chillers, CHP plant, seawater pumps, and DHW storage calorifiers.  Additional solar collectors could be located on other flat roofs in the host areas.  The roof of the workshop is being replaced and that alone has an area of around 1,000 m².

The calorifiers will be able to accept heat from the solar collectors as well as the CHP plant.  When solar-thermal DHW yields are low, say at night, the demand for cooling will also be below the peak and heat off the CHP/tri-generation plant can be directed away from the absorption chillers to the DHW calorifiers.  On an island like Soneva Fushi, it should be possible to heat DHW for free.

## Anaerobic digestion

Anaerobic digestion occurs when bacteria breakdown organic material into gas and a solid residual.  Soneva Fushi is thought to produce around half a tonne per day of dry “leafy” biomass and about half a tonne per day of dry food waste.  Feeding these into a well-run anaerobic digester should yield around 1,667 kWh of biogas per day.

The exact composition of the biogas will depend upon the nature of the organic matter, but would typically be between 50 and 75 percent methane, occupy a volume of between 150 and 300 cubic metres (if stored) and have a mass of between circa 100 and 200 kg.

By happy coincidence, the average daily electricity consumption of the two kitchens is 1,664 kWh (almost identical) and the daily average use of LPG is 152 kg (right in the middle of the anticipated biogas production).  It is reasonable to speculate, therefore, that all of the biogas could be gainfully used displacing all, or most, of LPG use or all energy associated with cooking.

There are two further advantages with anaerobic digestion: the first is that much of the gas captured and burnt is preventing methane entering the atmosphere, which is about 23 times more potent as a greenhouse gas than CO₂.  The other is that it reduces the associated waste streams to an inert compact residue.

The biogas, being as it is largely methane, is toxic and highly combustible and should be used directly rather than stored.  Although capture and storage technology does exist, the maintenance and supervision requirements are not well-suited to a small holiday island: better by far to consider better ways of using the gas as it is produced, for which there are a number of options and combinations, as below:

Option 1 - The biogas could be used to power a small combined heat and power (CHP) unit to generate about 17 kW of electricity and about 34 kW of heat.

Option 2 – Use the biogas within a simple hot water heater to produce about 70 kW of heat.

Option 3 – Drive a gas-fired absorption chiller to produce about 40 kW of cooling

Option 4 – Use biogas to displace LPG.  It is this option that provides the most varied opportunities and therefore requires more description.

In the context of the proposed overall energy strategy, the most carbon-efficient approach is to prioritise the biogas to displace LPG (Soneva Fushi cannot be carbon-zero if it’s burning LPG).  Although the estimated average production of biogas and use of LPG are similar, it is the usage profile that will determine the suitability of this option – three scenarios are considered:

- If the LPG demand is intermittent and “spikey”, then the biogas (which cannot be stored) will contribute very little, in which case one of the other options should be adopted.

- If however the LPG usage is, or can be made to be, very even and consistent, then the biogas might completely replace the LPG but do nothing else.

- If there are periods when the biogas can meaningfully displace the LPG, but other periods where it cannot (either because the demand is too small or too “spikey”), then the biogas should displace LPG when it can and be put to an alternative use when it cannot, such as options 1,2 or 3.

The optimum decision would rest on a detailed cost-benefit analysis when more is known about the LPG usage.

Figure 4.6.1 – Anaerobic digester with biogas CHP (showing  option 1)

## Electricity to laundries

Monthly electricity consumption for the year ending June 2009 has been supplied by Six Senses for the laundries (see graphs 4.7.1 and 4.7.2 below).

Graph 4.7.1 – Electrical load consumption for the laundries

Graph 4.7.2 – Electrical load consumption for the laudries per night-stay

Consistent with the site-wide electricity demand, and as expected, the consumption closely follows the island’s population size, although the energy used per night-stay is slightly lower at busy times:  this is likely to be due to some small common base loads, such as lighting, ventilation and the like, which will run regardless of population size making busy periods slightly more efficient per person.

Also received from Six Senses was an equipment list, the full extent of which is not reproduced here but summarised in table 4.7.1.

| Equipment | Power kW | Proposed energy source |
| --- | --- | --- |
| Air-conditioning | 13.7 | Site-wide chilled water (absorption chillers) |
| Clothes washers | 119.1 | solar-thermal |
| Hot water | 22.0 | solar-thermal |
| Clothes presses | 45.5 | Electricity (load too high for biogas) |
| Clothes dryers | 33.6 | Electricity (load too high for biogas) |
| Lighting | 1.3 | Electricity (could be |
| Fans | 3.8 | electricity |
| Misc | 9.1 | electricity |
| TOTAL | 101.1 |  |
| Table 4.7.1 - summary of equipment loads |  |  |

Graph 4.7.3 – connected power loads of laundry equipment, kW

In the proposed energy strategy, only lighting, fans and miscellaneous systems would have to be electrically powered, totalling 14.1 kW or 5.7 percent of the currently connected electrical load.

Clothes presses and driers could be gas-powered, but there is insufficient biogas generated on site for this, and because biogas cannot be transported (ref. Sub-section 4.3.2), the gas would have to be far-from-carbon-zero LPG.  For these reasons it is proposed to leave these as electrically powered.

The connected electrical load could therefore be reduced to 101 kW or 37.6 percent of the existing condition.

## Kitchens

Monthly electricity consumption for the year ending June 2009 has been supplied by Six Senses for the kitchens (see graphs 4.8.1 and 4.8.2 below).

Graph 4.8.1 – Electrical load consumption for the kitchens

Graph 4.8.2 – Electrical load consumption for the kitchens per night-stay

Like the laundries and overall site-wide electrical demand, the electricity demand is similarly sensitive to the island’s population count.

Unlike the laundries, no equipment list has been received for the kitchens, however the greater portion of the load is likely to be domestic hot water  (which is known to be electric), cooking and cooling.  Each of these loads can be transfered to low- and zero-carbon alternatives such as the island-wide chilled water system, solar-thermal domestic hot water systems and biogas from the aerobic digester.

## Lighting

There are no specific figures for annual lighting loads, and lighting usage is influenced as much by the idiosyncrasies of individual behaviour as it is by daylight penetration into buildings.  Despite these difficulties some basic modelling has been undertaken in order to estimate the order of magnitude (Appendix B).  The results of the analysis were an estimated 684 MWh (about 15 percent of current total electricity).

It is understood that fluorescent lighting in not favoured in guest areas because they do not create the right mood, they can’t be dimmed, they flicker, and they contain small doses of mercury which pollute the water table if not properly disposed of – which is just about impossible to do anywhere in the Maldives.  That said, fluorescents are used in the much brighter lit offices, but to do otherwise would result in very high electrical power loads – so the mercury-to-energy priority is arguably different.

Human beings universally like tungsten – there is something about their “incandescentcy” that seems to relax us, much like an open fire would.  This is not a modern adaptation but something innate; for instance the colour spectrum of tungsten lamps is so far skewed towards the red end of the visible spectrum that they should give everything a red tint.  However our eyes have adapted to this to the extent that we can differentiate between colours as effectively under tungsten lighting as we can under daylight.  In fact, tungsten is the reference against which the colour-rendering properties of all other lamps are judged.

Most fluorescent lamps have a colour spectrum that is towards the blue end of the spectrum which appears “cool”, invigorating, energetic and ideal for an office or a shop, but not for a romantic villa or restaurant.

Most of the problems of fluorescents can be resolved: they can have a warmer light similar to tungsten (see figure 4.9.1), and light fittings can be provided with high-frequency control gear that allows fluorescents to be dimmed whilst eliminating low-frequency mains flickering.  However high-frequency control gear is bulky and might be difficult to retro-fit, and there’s still the problem of the mercury.

Figure 4.9.1 – Colour spectra for “warm” fluorescent, tungsten and daylight

The recommendation of this report is to wait until LED lighting has matured to the extent that they have the same, or higher, light output per watt as compact fluorescent lamps.

LEDs can be warm similar to tungsten, they can be dimmed, they don’t flicker and they contain no lead.

Figure 4.9.2 watt LED lamp

If the villas do have a single master light switch, it’s not easy to find it, and so turning off all the lights when leaving or at night can be a real test of commitment.  It would be quite inexpensive to install a master switch in an obvious location by the front door that will interrupt the lighting circuit(s) at the distribution boards.  This could save around 200 MWh per year.

## Wind power

The wind power potential was assessed by XCO2 in a report they prepared for Six Senses in April 2008.  They extrapolated from 4.89 metres per second measured wind speed taken at 20m above sea level to conclude that the average annual wind speed at 48 m above sea level would be 5.4 meters per second, and at this speed a 900 kW wind turbine could meet about one-quarter of Soneva Fushi’s electrical demand.

CAS does not have the original wind speed data and the nearest wind speed data they do have is from the island of Minicoy, which may not be representative of Soneva Fushi.  CAS is not therefore able to verify XCO2’s conclusions.  As a due diligence exercise, CAS undertook their own wind speed extrapolation and calculated 5.3 m/s at a height of 48 m above sea level, which is almost identical to XCO2 answer of 5.4 m/s.  However 5.4 m/s is not very fast for a wind turbine, neither are consistently strong winds generally associated with the Maldives.

As a rule-of-thumb, a viable cost-effective wind turbine installation has a utilisation factor of about one-third.  So a 900 kW wind turbine, if well sighted, would produce an annual average power output of 300 kW and an annual total energy output of 2,628 MWh – which is about 60 percent of the current total electrical consumption.  If XCO2’s modelling found that only one-quarter the total consumption would be met, then the average annual power output of this 900 kW turbine would be about 125 kW, which is a utilisation factor of about one-eighth – this is very low indeed.

In addition to the poor economics, the aesthetics would not be to everybody’s tastes, as indicated in figure 4.10.1 with the Ms Liberty added for scale.  Even if the turbine was located on the adjacent island of Eydhafushi, as has been suggested, it’s going to be difficult to hide.

Figure 4.10.1 – the height of a 900 kW wind turbine to the top of the sweep is 67m (220 ft)

## Passive building measures

All of the buildings at Soneva Fushi are well designed for solar control.  Where they are weak is their high air permeability.  Ideally the buildings would have much tighter detailing and no slatted vents.  However to retrofit higher standards in each building would be expensive and disruptive.

No matter how well the buildings are sealed or otherwise treated, supplementary cooling is still going to be necessary, albeit at a slightly smaller size and slightly lower cost.

The only significant reduction will be to the annual cooling load, but if the cooling is free off the absorption chillers, this is of negligible benefit.

The proposal therefore is to optimise the design of replacement and refurbished buildings.  For instance, it is understood that the Rehendi are being replaced.  If so, this is an excellent opportunity to introduce additional passive measures.  The following are recommended in addition to the Soneva Fushi norm:

- New buildings should be designed and constructed to achieve a maximum air leakage rate of 5 m³/h/m² of total external envelope at an applied pressure of 50 Pa.

- Buildings should be designed to allow cross-flow ventilation

- Magnetic switches on vents, doors and windows should disable the air-conditioning.

There is a natural synergy here with the long-term strategy of increasing the application of PV:

- The cooling loads will progressively reduce as the building stock is improved, and

- The cooling available off the tri-generation plant reduces as the PV increases.

## Low-carbon building-integrated cooling solutions

There are all sorts of ways of cooling buildings other than the ubiquitous vapour compression chiller.  None of them are new, although they’re frequently given different names in different countries or by different manufacturers.  Many of them are very effective and the writer has recommended many of them in applications all over the world.  However the purpose of this report is not to produce an encyclopaedia of air-conditioning technologies, but rather to report on recommended strategies.

The difficulty with most of the building-integrated alternatives to the vapour compression “split” unit, such as desiccant and hygroscopic air cooling methods, is that they’re too bulky and complex for small buildings such as villas and boutique-type shops.  Desiccant air cooling systems require a heat source for purging in much the same way that absorption chillers do.  In fact, absorption chillers are a form of desiccant cooling, but they are more thermally efficient that desiccant air systems.

## Desalinated water

Soneva Fushi currently uses a Reverse Osmosis (RO) process to purify seawater into drinking water.  In this process, electrical energy is required to pump the water through a series of membranes.  Whilst this is comparatively cheap it is also quite energy intensive.  To purify one cubic metre of water requires circa 5.62 kWh of electricity.  With the existing diesel generators, the embodied carbon content of Soneva Fushi potable water is about 4.7 kg CO₂ per m³.   The low energy alternative is solar desalinisation.

The solar desalination process is based on evaporation of salt water and the subsequent condensation of the generated steam using only solar power.  The produced steam is virtually clear and does not carry any solvents.  Following condensation, salt-free fresh water is collected.

In the process, seawater is heated by the sun or by use of waste heat, supplied via heat exchangers.  The heated salty water enters an evaporation chamber from where it evaporates from antibacterial fleece surfaces. The produced steam is transported to the condenser in a second step, without additional energy demand.

Figure 4.13.1 – solar desalination schematic

Figure 4.13.2 – example of solar desalination plant

Currently the RO plant is responsible for 8.5 percent of annual electricity usage, but to avoid that energy with solar desalination would require an area of 540 m² to accommodate the necessary solar collectors.  To put matters into context, using solar-thermal panels to displace electric water heating is almost seven times more viable than using the same panels to displace electricity used in the RO plant.

Rather than concentrating on lower energy desalination, the focus instead should be on using desalinated water more frugally.  Currently it is used for almost everything other than lavatory flushing in the host accommodation, including lavatory flushing in the guest areas, laundry and bathing.

The desalinated water consumption per night-stay averages 344 litres.  There is no volumetric breakdown of where this water is used, therefore calculations were done to estimate the elemental usage, as below.

| Guest WCs |  |  |
| --- | --- | --- |
| Flushes per day per night-stay | 3 | estimate |
| Flush volume | 9 litres | standard upper limit |
| Total usage per night-stay | 27 |  |
| Annual guest night-stays | 37,458 |  |
| Annual flushing water | 1,011 m3 | 2% |
| Guest showers |  |  |
| Showers per night-stay | 1.5 |  |
| shower flow rate | 0.14 L/s |  |
| Shower duration | 5 mins | UK average is about 3 mins |
| Total usage per shower | 42 litres |  |
| Total usage per night-stay | 63 litres |  |
| Annual night-stays | 192,816 |  |
| Annual showering water | 12,147 m3 | 18% |
| Guest bathing |  |  |
| Baths per night-stay | 1 |  |
| Volume | 80 litres |  |
| Total usage per night-stay | 80 litres |  |
| Annual guest night-stays | 37,458 |  |
| Annual showering water | 2,997 m3 | 5% |
| All catering |  |  |
| Total meals served | 299,847 |  |
| Water used per meal | 14 litres | (source: CIBSE Guide, Table 2.11) |
| Annual catering water | 4,198 m3 | 6% |
| All drinking water |  |  |
| Per night stay | 2.5 litres | (source: UK Institute of Plumbing Guide, page 74) |
| Annual night-stays | 192,816 |  |
| Annual drinking water | 482 m3 | 1% |
| Laundry, irrigation, other | 45,481 | 69% |

Obviously not even the guests need to flush drinking water down their lavatories or put in their baths, however they most likely want potable water for everything else, and it’s not cost-effective to run a separate set of water pipes to each villa just to save an estimated seven percent, especially when there are so many richer pickings to be had more easily elsewhere.

These calculations are showing that water usage for the whole island’s catering and drinking water needs, plus all water used within the villas, only accounts for about one-third of the total desalinated water usage.  The other approximately two-thirds is used for laundries and other purposes that could use water treated to a much lower standard using much less energy.

To capitalise on this proposal requires an island-wide non-potable water mains to be provided.  The ideal time to do this is when installing the island-wide chilled water and domestic hot water networks.

## Biochar

Soneva Fushi has an estimated 250 kg of dry timber biomass per day.  If this is pyrolysised about 100 tonnes of CO₂ will be sequestrated each year.

Pyrolysis is the process of burning something in the absence of oxygen.  There are two stages to the process.  In stage one the biomass feedstock is placed in a container with a chimney but otherwise sealed.  A fire is lit beneath the biomass, but because the biomass container is sealed, no oxygen can enter and so the biomass is being heated in the absence of oxygen.  Stage one lasts about eight hours during which time mostly water vapour is driven off.

In stage two toxins start to be driven off, such us methane which is a greenhouse gas (GHG) 23-times more potent than CO₂.  Rather than allow these into the atmosphere, the chimney is blocked and a damper opened to the fire box.  The toxins are thus burnt in the fire box, at which point the process becomes self-powering and the toxins are either bound within the biochar or released as less harmful gases, such as CO₂.  Stage two lasts for about four hours.

Biocharing prevents the biomass simply decomposing into CO₂ and methane by binding up half the GHGs into the biochar and converting the other half of methane into the less damaging CO₂.

The biochar can then be mixed with organic waste to make an excellent fertiliser.  Fish waste, which is abundant in the Maldives, is one of the best possible organic wastes to mix with the biochar.

The biochar fertiliser can either be used on Soneva Fushi or sold. It is evident that increased food production on the island reduces dependency on imported products, which will also reduce the carbon footprint. This reduction of the carbon footprint is an additional benefit as this is best studied after the food production process has commenced.

Figure 4.14.1 – CO₂ sequestration

# Analysis and Results

## Method and approach

Six Senses have provided detailed annual-monthly breakdowns of diesel, water, electricity and LPG consumption for the island as a whole; annual-monthly breakdowns of electricity consumption for the restaurants and laundries; annual electricity consumption for the water desalination plant and the annual-monthly population of hosts and guests.  These data are the only data known for certain.

The better the breakdown of information, the more reliable the analysis will be, therefore energy modelling using computer software has been undertaken to estimate electricity used for cooling and lighting (Appendix B).

The actual energy consumption for cooling and lighting will vary depending upon the weather, number of guests and hosts and peoples’ individual behaviour.  So the actual energy consumption will vary all the time and there is no definitive correct answer against which to compare the accuracy of the computer models.

The energy models are useful insofar as they give a very good indication of what the energy consumption would be under a range of likely scenarios, which in turn allows different energy strategies to be tested.  What matters most of all is that the right design, procurement and management decisions are taken.

## Current scenario

Using the data received from Six Senses and the modelling data from Appendix B for cooling and lighting, graphs 5.2.1 and 5.2.2 were prepared for the island as it was year ending June 2009 (these graphs were also used in section 3).

To these data the planned additional cooling to the host area accommodation was added and then the favoured energy reduction strategies described in Section 4 are progressively applied.  The graphs were re-cast to show the incremental benefits and presented in sub-sections 5.4 and 5.5.

Graph 5.2.1 – monthly electricity usage, current (as graph 3.2).

Total electricity consumption = 4,355,346 kWh

Grpah 5.2.2 – monthly electricity usage, current (as graph 3.3)

Electricity per night-stay = 23 kWh

| Fuel | Emissions |  |
| --- | --- | --- |
| Diesel/electricity | 3,630 | tonnes CO₂ |
| LPG | 152 | tonnes CO₂ |
| Total | 3,782 | tonnes CO₂ |

Table 5.2.1 – CO₂ footprint

## Cooling to host accommodation added

Graph 5.3.1 – monthly electricity usage with additional cooling to host accommodation.

Total electricity consumption = 4,601,534 kWh

Grpah 5.3.2 – monthly electricity usage with additional cooling to host accommodation

Electricity per night-stay = 24 kWh

Changes:

Additional cooling applied to host area accommodation using conventional cooling (split systems)

| Fuel | Emissions |  |
| --- | --- | --- |
| Diesel/electricity | 3,835 | tonnes CO₂ |
| LPG | 152 | tonnes CO₂ |
| Total | 3,987 | tonnes CO₂ |

Table 5.2.2 – CO₂ footprint

## Demand reduction, solar-thermal, DHW, PV and anaerobic digesters

Graph 5.4.1 – monthly electricity usage with demand savings, solar-thermal DHW and PV

Total electricity consumption = 3,552,830 kWh

Grpah 5.4.2 – monthly electricity usage with demand savings, solar-thermal DHW and PV

Electricity per night-stay = 18 kWh

Changes:

demand reduction for potable water, lighting, kitchen and laundry electricity, provision of PV and anaerobic digesters to displace LPG, and solar-thermal domestic hot water (DHW).

| Fuel | Emissions |  |
| --- | --- | --- |
| Diesel/electricity | 2,961 | tonnes CO₂ |
| LPG | 0.00 | tonnes CO₂ |
| Total | 2,961 | tonnes CO₂ |

Table 5.4.1 – CO₂ footprint

## As 5.4 but tri-generation added

Graph 5.5.1 – monthly electricity usage as 5.4 but added tri-generation

Total electricity consumption = 2,406,713 kWh

Grpah 5.5.2 – monthly electricity usage as 5.4 but added  tri-generation

Electricity per night-stay = 12 kWh

| Fuel | Changes: As 5.4 but added tri-generation Emissions |  |
| --- | --- | --- |
| Diesel/electricity | 2,006 | tonnes CO₂ |
| LPG | 0.00 | tonnes CO₂ |
| Total | 2,006 | tonnes CO₂ |

Table 5.4.1 – CO₂ footprint

## Energy monitoring and reduction

The metered and modelled electrical loads have been reduced from 3,068,091 kWh to 1,271,984 kWh; a reduction of nearly 60 percent.  After the implementation of all of the reduction strategies, the load labelled “other” is larger than all of the others combined at 1,287,255 kWh.

In order to tackle this load, a detailed breakdown is required.  To this end, it is recommended that electricity sub-metering strategy is developed.  As a minimum, meters should be installed on each building and plantroom, and any single load over 20 kW.

The meters should be read at the same time each month and used to gather data to inform further energy reduction initiatives.  If the “other” loads can also be reduced by 60 percent, the total electricity of the island would reduce to an estimated  1,790,407 kWh per year and 1,492 tonnes of CO₂.  However this is highly speculative and therefore this possible potential saving is not carried forward to the next carbon reduction stage.

## Biodiesel

The current annual CO₂ emissions for the island have been assessed at 3,782 tonnes.  Introducing the host cooling increases this to an estimated 3,987 tonnes CO₂ per year, and after the adoption of the energy reduction measures identified in this report, the emissions drop to an estimated 2006 tonnes of CO₂ per year - all from combusting diesel to generate 2,406,713 kWh electricity.

The CO₂ reduction is therefore approximately 50 percent.  It is likely that the emissions can be reduced further by attacking the unidentified electrical loads, but no allowance can be made for this without knowing what the electricity is being used for.  However, no matter how much the electricity demand is further reduced, so long as there is a demand for electricity from diesel-powered generators, the island will not be carbon-zero.

The next step in the strategy therefore is to replace the diesel with bio-diesel.  Bio-diesel isn’t carbon-zero either due to the energy used in processing and shipping, but its carbon emissions factor is very small at around 0.025 kg CO₂ per kWh.

Using an electrical generator that’s 30 percent efficient, the remaining CO₂ emissions are:

2,407 x 1/0.3 x 0.025 = 200 tonnes CO₂ per year

This is very low, but it’s not carbon-zero.

## Biochar

Biocharing sequestrates 100 tonnes of CO₂ per year, leaving Soneva Fushi with a residual CO₂ footprint of 100 tonnes per year.  That is a reduction of 97 percent, but still not quite carbon-zero.

## Enhanced forest productivity

The final step in the quest for a carbon-neutral Soneva Fushi is to enhance the productivity of the forest to sequestrate more carbon dioxide.  Using the biochar fertiliser and optimised forest stewardship, the carbon dioxide sequestration of the forest can be enhanced by between 1 and 4 tonnes CO₂ per hectare per year.

Soneva Fushi has at least 30 hectares of forest.  At 4 tonnes CO₂ per hectare the additional carbon dioxide sequestration is 120 tonnes, which is more than the 100 tonnes required.

# Recommendations

- Reduce energy consumption through simple energy-efficient measures, such as better light-switching, efficient use of potable water, better energy metering and thorough energy auditing.

- Provision of site-wide solar-thermal domestic hot water (DHW).

- Procurement of “ethical” biodiesel.

- Switching from electricity to solar-thermal DHW or biogas wherever possible in kitchens, laundries and other DHW usage.

- Installation of 70 kW photovoltaics panels (already installed).

- Replace the existing electrical generators, which are too large, with smaller biodiesel-fired Combined Heat and Power (CHP) units.

- Provide an island-wide chilled water network with central absorption chillers powered from the waste heat off the new biodiesel CHP units and water-cooled using a refurbished seawater system.

- Biochar all branches and other “woody” biomass.

- Use organic digesters to gasify food waste and “leafy” biomass.  The gas is then used to displace LPG and/or to reduce electrical loads through micro CHP – all dependent upon further analysis of the loads profiles.

- Progressively introduce PV modules on the flat roofs of host areas, especially as battery technology improves and prices reduce.  This will have the effect of reducing the output of the tri-generation plant.

- New villas to be built to higher standards of air permeability to reduce cooling loads on the tri-generation plant, especially as output reduces with the higher deployment of PV.

- If necessary, provide an alternative heat source for the absorption chillers as the heat from the CHP plant progressively reduces with the deployment of PV over time.  This could be concentrated solar power, evacuated tubes or hydrogen fuel cells.

|  | step 1 | step 2 | step 3 | step 4 | step 5 | step 6 | step 7 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Description | 3782 | 3987 | 2961 | 2006 | 200 | 100 | 0 |
| Current | yes | yes | no | no | no | no | no |
| Add host cooling | no | yes | yes | yes | yes | yes | yes |
| Reduce RO water | no | no | yes | yes | yes | yes | yes |
| Solar-thermal DHW | no | no | yes | yes | yes | yes | yes |
| Photovoltaics | no | no | yes | yes | yes | yes | yes |
| anaerobic digesters | no | no | yes | yes | yes | yes | yes |
| master light switch in villas | no | no | yes | yes | yes | yes | yes |
| Tri-generation | no | no | no | yes | yes | yes | yes |
| Biodiesel | no | no | no | no | yes | yes | yes |
| Biochar | no | no | no | no | no | yes | yes |
| Enhanced forest productivity | no | no | no | no | no | no | yes |

Table and graph 6.1 – sequential reduction in CO₂

Table and graph 6.2 – sequential reduction in CO₂ (bar stacked)

Figure 6.2 – Schematic of proposed integrated carbon reduction strategy

# Appendices

## Appendix A – Calculation of proposed CO₂ emissions factors

| Fuel | Carbon emissions factor |  | Source |
| --- | --- | --- | --- |
| Diesel | 0.263 | kg CO₂/kWh | 1 |
|  | 2.639 | kg CO₂/litre | 1 |
|  | 3164 | kg CO₂/tonne | 1 |
| Biodiesel | 0.025 | kg co2/kWh | 4 |
| LPG | 0.225 | kg CO₂/kWh | 1 |
|  | 1.495 | kg CO₂/litre | 1 |
|  | 2.932 | kg CO₂/kg | 5 |
| Petrol | 0.252 | kg CO₂/kWh | 1 |
|  | 2.304 | kg CO₂/litre | 1 |
|  | 3423 | kg CO₂/tonne | 1 |
| Electricity | 0.834 | kg CO₂/kWh | 2 |
| Water | 4.688 | kg CO₂ per m³ | 3 |
| Project CO₂ emissions factors |  |  |  |

| Source 1 |  |  |  |  |
| --- | --- | --- | --- | --- |
| 2009 Guidlines to Defra/DECC's GHG Conversion Factors for Company Reporting |  |  |  |  |  |
| Source 2 |  |  |  |  |
| UK Building Regulations - more specific factors to be calculated when fuels being chosen |  |  |  |  |  |
| Source 3 |  |  |  |  |
| On-site electricity CO₂ emissions factor |  |  |  |  |
| 4,355,346 | kWh electricity from | 1,375,564 | litres of diesel |  |
| 1,375,564 | litres of diesel at | 2.639 | kg CO₂/litre |  |
| 3630251 | kg CO₂ |  |  |  |
| 3630251 | kg CO₂ for | 4,355,346 | kWh electricity |  |
| 0.833516 | kg CO₂ per kWh |  |  |  |
| Source 4 |  |  |  |  |
| Conversion of LPG from kg CO₂ / L to kg CO₂ / kg |  |  |  |  |
| 1.495 | kg CO₂/litre |  |  |  |
| density | 0.51 | kg/litre |  |  |
| 1.00 | kg is | 1.96 | litres |  |
| 1.495 | x | 1.96 | litres |  |
| 2.932 | kg CO₂/kg |  |  |  |
| Source 5 |  |  |  |  |
| On-site RO plant |  |  |  |  |
| 66316000 | litres of water from | 373000 | kWh electricity |  |
| 373000 | kWh electricity at | 0.834 | kg CO₂/kWh |  |
| 310902 | kg CO₂ |  |  |  |
| 310902 | kg CO₂ for | 66316000 | litres water |  |
| 0.00469 | kg CO₂ per litre |  |  |  |
| 4.69 | kg CO₂ per m³ |  |  |  |

## Appendix B – energy modelling

## Thermal modelling

Cooling is likely to be the single largest electrical demand on the island, therefore the energy strategy will be effected by the simultaneous peak demand and profile.

Thermal modelling an island resort such as Soneva Fushi is especially challenging because the loads are very sensitive to human behaviour, which can only be estimated.  The challenge is met by simulating the buildings over a range of likely behavioural traits, such as the operational hours of cooling, how many villas are let, etc.

It is important that the energy strategy is viable across the whole range of likely scenarios, it is less important to predict which scenario is closer to the real world, especially as the real world situation will be changing constantly.

The approach has been to model about 80% of the loads.  The remaining 20% is distributed across a wide range of small buildings for which drawings and survey data are not available

With acceptable accuracy, this 20% is assumed to follow the same cooling profile as the modelled 80%.

Some buildings were taken to be representative of others, for instance the Dhondheeni has been taken as representative of all similar host accommodation, although it was modelled with both east-west and north-south orientations.

The next few pages give details of what has been modelled, which buildings have been treated as representative of others and the total number of each type of building.

Note 1: In fact there are only two of these; one on the east and the other on the west.  A third was added to make allowance for the owners’ villa for which no details have been found.  The models for the Treehouse, Retreat and Jungle reserve are preliminary because they lack accurate elevation details, this in turn is because they were not available to be surveyed during the last site visit.  Without accurate elevation details, there is no value in modelling the two different orientations.

Host living accommodation, based on Dhondheeni

If oriented east-west,

cooling intensity is 56 W/m²

annual cooling is 185 kWh/m²

If oriented north-south,

cooling intensity is 49 W/m²

annual cooling is 152 kWh/m²

Using the site plan and floor area schedule, the following orientations were used:

9,149 m² east-west

2,178 m² north-south

Peak cooling load = 619 kW (whole resort)

Fan-coil schedule shows installed capacity of 411 kW

Annual cooling demand = 2,024 MWh (whole resort)

Office building, based on admin office

Peak cooling intensity = 80 W/m²

Annual cooling intensity= 162 kWh/m²

Total office space = 1,244 m² (whole resort)

Peak cooling load = 99.5 kW (whole resort)

Fan-coil schedule shows installed capacity of 103 kW

Annual cooling demand = 202 MWh (whole resort)

Retail, based on retail in admin building

Peak cooling intensity = 104 W/m²

Annual cooling intensity = 217 kWh/m²

Total retail space = 450 m² (whole resort)

Peak cooling load = 46.8 kW (whole resort)

Fan-coil schedule shows installed capacity of 60 kW

Annual cooling demand = 98 MWh (whole resort)

Sensitivity analysis, host accommodation

Sensitivity analysis, guest accommodation

Sensitivity analysis, office accommodation

Sensitivity analysis, retail

Two bedroom Crusoe

One bedroom Crusoe

## Lighting calculations

There are many idiosyncrasies with lighting, especially around individual behaviour in villas.  Although a precise answer can never be obtained, not least because the reality changes from year-to-year and from guest-to-guest, it is possible to understand the order of magnitude.  Certainly it is possible to narrow the estimation down to a range, below which it is certainly too low and above which it is certainly too high.  The spreadsheet over show the assumptions made.

## Appendix C – weather data

Three sources:

- hourly-annual weather data file for Minicoy (c.218 km north Male)

- hourly-annual weather data file for Male’ airport, excludes global radiation (c.113 km south)

- XCO2 graphical and tabular data for Soneva Fushi, excludes wet-bulb temperature

XCO2 data

October 2006 to April 2008

Measured:

- wind speed and direction

- dry-bulb temperature

- relative humidity

- global radiation

Concerns with data:

- only one sensor per parameter

- measurements only for 18 months

- birds have “interfered” with wind speed measuring – what else?

- obvious defective with RH sensor, could other sensors be wrong too but less dramatically?

- Questionable global radiation data

- No wet-bulb data – essential for evaporative cooling analysis